## PAT
PAT
Ref No | Last Known Location | Description | Manufacturer | Model/Type | Volts | Watts/Amps | Class | Test Date | Re-test Interval | Expiry Date | New to CTPG | Comments
1 | Broad Street | Work Lamp (Tube Type) | Defender | Fluorescent | 230V | 38W | 2 | 13.9.19 | 12 months | 13.9.20
2 | Broad Street | Work Lamp (Tube Type) | Defender | Fluorescent | 230V | 38W | 2 | 13.9.19 | 12 months | 13.9.20
3 | Docks | Work Lamp (Tube Type) | Defender | Fluorescent | 230V | 38W | 2 | 20.9.19 | 12 months | 20.9.20 |  | Damaged plug replaced Jan 18
4 | Broad Street | Work Lamp (Incandescent) | SFD | Tungsten | 230V | 250W | 1 | 21.7.19 | 12 months | 21.7.20
5 | Broad Street | Work Lamp (Incandescent) | Defender | Tingsten | 230V | 250W | 1 | 21.7.19 | 12 months | 21.7.20
6 | Broad Street
7
8 | Broad Street | Portable Power Drill | MAC Allister | MSK600 | 220-240V | 600W | 2 | 8.8.18 | 12 months | 8.8.19 |  | Similar unit failed leakage test Dec 2016
9 | Broad Street | Portable Power Drill | Black & Decker | H26 15 | 240V | 1.6A/370W | 2 | 6.9.19 | 12 months | 6.9.20 | 17.9.17 | Leakage 160MOhm
10 | Broad Street | Portable Power Drill | Sealey |  | 200-250V |  | 2 | 6.9.19 | 12 months | 6.9.20 |  | 115 MOhm Leakage
11 | Broad Street | Portable Power Drill | Black & Decker | KD791 | 230V | 3.4A/750W | 2 | 6.9.19 | 12 months | 6.9.20
12 | Broad Street | Portable Power Drill | Power Craft |  |  |  | 2 | 6.9.19 | 12 months | 6.9.20
13 | Broad Street | Portable Power Drill | Atlas Copco | 500R | 240V | 550W | 2 | 7.8.18 | 12 months | 8.8.19 |  | Cable Damage 12/4/17
14
15 | Broad Street | Work Lamp (Tube Type) | Tull Wonderlight | T2611D | 240V | 10W | 2 | 21.7.19 | 12 months | 21.7.20
16 | Broad Street | Angle Grinder | Large |  | 240V |  | 2 | 6.9.19 | 12 months | 6.9.20
17 | Broad Street | Angle Grinder | BOSCH | HD720 | 230V |  | 2 | 6.9.19 | 12 months | 6.9.20 |  | Case damage- not safety critical
18
19
20 | Broad Street | Submersible pump | Royal | TMP255 | 230V |  | 2 | 13.9.19 | 12 months | 13.9.20
21 | Broad Street | Portable Jigsaw | MAC Allister | MJS750L | 230V | 750W | 2 | 6.9.19 | 12 months | 6.9.20
22 | Broad Street | Portable Jigsaw | WICKES | WJS710L | 230V | 750W | 2 | 6.9.19 | 6 months | 6.9.20
23 | Broad Street | Portable Jigsaw | BOSCH | CAO770D | 220-250V | 500W | 2 | 6.9.19 | 12 months | 6.9.20
24
25 | Broad Street | Soldering Iron | ???LOGIC |  | 240V | 30W | 1 | 21.7.19 | 12 months | 21.7.20 |  | 130 Mohm Leakage
26 | Broad Street | Soldering Iron | Weller |  | 240V |  |  | 21.7.19 | 12 months | 21.7.20
27 | Broad Street | Battery Charger/Starter | DRAPER | 1196 | 240V |  | 1 | 6.9.19 | 12 months | 6.9.20
28 | Broad Street | Portable paint sprayer | Performance Power | PP8400 | 240V | 400W | 2 | 13.9.19 | 12 months | 13.9.20
29 | Broad Street | Multi Tool drill | Performance Power | 97810A | 240V |  | 2 | 03.03.21 | 12 months | 03.03.21 | Previous test 10.08.17
30
31
32
33
34 | Broad Street | Worklamp | Stadium |  | 240V | 60W | 2 | 13.9.19 | 12 months | 13.9.20 |  | Bish
35 | Broad Street | Extension Cable | POWER PLUS | 50m | 230V | 13A | 1 | 6.9.19 | 12 months | 6.9.20 |  | Plug repaired 6.9.19
36 | Broad Street | Extension Cable | MASTER PLUG | 50m | 230V | 13A | 1 | 20.9.19 | 12 months | 20.9.20 |  | Earth Impedance 0.4 Ohm
37 | Broad Street | Extension Cable | MASTER PLUG | 30m | 230V | 13A | 1 | 21.7.19 | 12 months | 21.7.20 |  | Earth Impedance 0.4 Ohm
38 | Broad Street | Extension Cable | JOJO | 12m | 240V | 13A | 1 | 12.3.20 | 12 months | 12.3.20
39
40
41 | Broad Street | Extension Cable | POWER PLUS | 50m | 230V | 13A | 1 | 17.7.19 | 12 months | 17.7.20 |  | Earth Impedance 0.8 Ohm
42 | Broad Street | Extension Cable | PIFCO | 4m | 230V | 13A | 1 | 21.7.19 | 12 months | 21.7.20 |  | Pass after repair
43 | Broad Street | Extension Cable | Unknown | 30m | 230V | 13A | 1 | 21.7.19 | 12 months | 21.7.20
44 | Broad Street | Extension Cable | Unknown | 25m | 230V |  | 1 | 19.11.19 | 12 months | 19.11.20 |  | Shortened to eliminate damage
45
46
47
48
49 | Broad Street | Portable Belt Sander | BLACKSPUR |  | 230V |  | 2 | 21.7.19 | 12 months | 21.7.20 |  | Pass after repair
50 | Broad Street | Portable Sander | Challenge | M53585 | 230V | 140W | 2 | 21.7.19 | 12 months | 21.7.20
51
52 | Broad Street | Light Duty Steam Cleaner | Hoover | SSNHA 1000 | 230V | 1200W |  | 8.8.18 | 12 months | 8.8.19
53 | Broad Street | Heat Gun | Black & Decker |  | 230V |  | 1 | 6.9.19 | 12 months | 6.9.20 |  | 185Mohm Leakage
54 | Broad Street | Heat Gun | Earlex |  | 230V |  | 2 | 6.9.19 | 12 months | 6.9.20
55 | Broad Street | Paint Spray Gun |  |  |  |  | Unknown | Due | 12 months
56 | Broad Street | Radio Receiver (Pit Area) | Sanyo |  | 230V |  | 2 | 6.9.19 | 12 months | 6.9.20
57 | Broad Street | Polisher/Buffer | HALFORDS |  | 230V |  | 2 | 6.9.19 | 12 months | 6.9.20
58
59
60 | Broad Street | Mains short extension & 4-way splitter | Attached to Pit Trolley |  | 240V |  | 1 | 13.9.19 | 12 months | 13.9.20
61 | Broad Street | Steam Cleaner | Karcher | HD5580 | 230V |  | 1 | 13.9.19 | 12 months | 13.9.20
62 | Broad Street | Mains short extension & 4-way splitter | Unknown |  | 230V | 13A | 1 | 21.7.19 | 12 months | 21.7.20 |  | Earth Impedance 0.4 Ohm
63
64
65
66
67 | Broad Street | Rectangular Sander | Black & Decker | KA300 | 230V | 135W | 2 | 21.7.19 | 12 months | 21.7.20
68 | Broad Street | Rectangular Sander | Black & Decker |  | 230V |  | 2 | 21.7.19 | 12 months | 21.7.20
69 | Broad Street | Rectangular Sander | Black & Decker |  | 240V | 0.8A | 2 | 21.7.19 | 12 months | 21.7.20
70 | Broad Street | Detail Sander | Parkside | PHS160B2 | 240V | 160W | 2 | 21.7.19 | 12 months | 21.7.20
71 | Broad Street | Electric Planer | Power Craft | EH900 | 240V | 900W | 2 | 03.03.21 | 12 months | 03.03.21 |  | Previous test 10.08.17
72 | Broad Street | Handheld Circular Saw | Black & Decker | KS266 | 240V | 2.2A | 2 | 21.7.19 | 12 months | 21.7.20
73 | Broad Street | MIG Welder | CEBORA |  |  |  |  | 13.9.19 | 12 months | 13.9.20
74
75 | Broad Street | MIG Welder | SIP |  | 240V |  | 1 | 20.9.19 | 12 months | 20.9.20 |  | Plug repair 20.9.19
76 | Broad Street | Bench Pillar Drill | Parkside |  | 230V | 500W | 1 | 21.7.19 | 12 months | 21.7.20
77 | Broad Street | ARC Welder | Clarke | 190 | 240V |  | 1 | 13.9.19 | 12 months | 13.9.20 |  | Plug repair 13.9.19
78 | Broad Street | Power Drill | B & Q | PHD710A | 240V | 710W | 2 | 19.11.19 | 12 months | 19.11.20 |  | First test 17.1.18
79 | Broad Street | Angle Grinder | Makita | GA4530R | 230-240V | 720W | 2 | 6.9.19 | 12 months | 6.9.20 |  | New Jan 2018
80 | Broad Street | Heat Gun | Black & Decker | HG991/H2A | 240V | 1200W | 2 | 20.9.19 | 12 months | 20.9.20 |  | First test 17.1.18
81 | Broad Street | Rip Saw | Black & Decker | DN54-H3 | 230V | 450W | 2 | 17.7.19 | 12 months | 17.7.20 |  | First test 17.1.18
82 | Broad Street | Jigsaw | Black & Decker | DN31S/H5 | 240V | 330W | 2 | 20.9.19 | 12 months | 20.9.20 |  | First test 17.1.18
83 | Broad Street | Power Drill | Black & Decker | BD163V-H1C | 240V | 550W | 2 | 20.9.19 | 12 months | 20.9.20 |  | First test 17.1.18
84 | Broad Street | Portable compressor | Powercraft | PC220108 | 240V |  | 2 | 6.9.19 | 12 months | 6.9.20
85
86
87
88
89 | Broad Street | ARC Welder | Powercraft | ARC145 | 240V | 40A | 2 | 13.9.19 | 12 months | 13.9.20
90 | Broad Street | Angle Grinder | Hitachi | G12SR3 | 240V | Unknown | 2 | 20.9.19 | 12 Months | 20.9.20 |  | Second hand arr 30.1.18
91 | Broad Street | Drill charger | Makita | HP347D | 240V |  | 2 | 05.10.19 | 12 months | 05.10.20 | 2019-10-05 | New 05.10.19
92
93
94
95
96
97
98
99
100 | Docks | Work Lamp (LED rechargable) | Defender | E206010 | 240V |  |  | 08.04.20 | 12 months | 08.04.21 | 2020-04-08
101 | Docks | Work Lamp (Tube Type) | Defender |  | 240V |  |  | 20.9.19 | 12 months | 20.9.20
102 | Docks | Work Lamp (Incandescent) | Unknown | F1101 | 240V |  |  | 20.9.19 | 12 months | 20.9.20
103
104 | Docks | Air compressor | Clarke |  | 240V |  | 1 | 20.9.19 | 12 months | 20.9.20 | Fixed Equipment
105
106
107 | Docks | Extension Cable 1 | PIFCO | 50m | 240 |  |  | 03.03.20 | 12 months | 03.03.21 | 2020-03-03
108 | Docks | Battery Charger/Starter 1 | Clarke 520 |  | 240V |  |  | 20.9.19 | 12 months | 20.9.20
109 | Docks | Extension Cable 3 | PIFCO | 50m | 240V |  |  | 24.10.19 | 12 months | 24.10.20 | 2019-10-24 | New 24.10.19
110
111
112 | Docks | Grinder | Workzone | WTS125 | 240V | 150W |  | 20.9.19 | 12 months | 20.9.20
113 | Docks | Bench Grinder | NuTool | CH152 | 240V | 150W |  | 20.9.19 | 12 months | 20.9.20
114 | Docks | Ext Lead | Homebase |  | 240V |  |  | 20.9.19 | 12 months | 20.9.20
115 | Docks | Steam Cleaner | Karcher | HDS801C | 240V |  |  | 20.9.19 | 12 months | 20.9.20
116 | Docks | Drill |  |  | 240V |  |  | 20.9.19 | 12 months | 20.9.20
201 | Broad Street | Air Compressor | CLARKE | EASYAIR | 230V | 3HP | 1 | 6.9.19 | 12 months | 6.9.20 | Fixed Equipment | Visual only
202 | Broad Street | Bandsaw | SIP |  | 240V |  | 1 | 6.9.19 | 12 months | 6.9.20 | Fixed Equipment
203 | Broad Street | Bench grinder 1 | CLARKE | CBG8RWC | 230V | 375W | 1 | 21.7.19 | 12 months | 21.7.20 | Fixed Equipment | Plug reterminated 12.8.17
204 | Broad Street | Bench grinder 2 | HILKA | 6" | 240V | 370W | 1 | 6.9.19 | 12 months | 6.9.20 | Fixed Equipment
205 | Broad Street | Bench grinder 3 | PARKSIDE | PDS200A | 230V | 200W | 1 | 6.9.19 | 12 months | 6.9.20 | Fixed Equipment
206 | [10 empty] | Fixed Equipment
207 | Broad Street | Parts Degreaser |  |  | 240V |  | 1 | 6.9.19 | 12 months | 6.9.20 | Fixed Equipment | 76 MOhm Leakage
208 | Broad Street | Circular Bench Saw | Titan | TTB674 TAS | 240 | 1500W | 1 | 6.9.19 | 12 months | 6.9.20 | Fixed Equipment | New 11.4.18
209 | Broad Street | Pillar Drill | HILKA |  | 240V | 120W | 1 | 13.9.19 | 12 months | 13.9.20 | Fixed Equipment | New plug 13.9.19
301 | Broad Street Mess Room | Kettle (Black) | TESCO |  |  |  | 2 | 12.5.19 | 12 months | 12.5.20
302 | Broad Street Mess Room | Kettle (White) | ASDA | XB6538 | 240 | 2200W | 1 | 12.5.19 | 12 months | 12.5.20 |  | First test 11.4.18
303 | Broad Street Mess Room | Toaster (chrome) | TESCO | 2T15SS | 240 | 700-800W | 1 | 12.5.19 | 12 months | 12.5.20 |  | First test 11.4.18
304 | Broad Street Mess Room | Toaster (white) | TESCO |  |  |  | 1 | 12.5.19 | 12 months | 12.5.20
305
306 | Broad Street Mess Room | Summer cooling fan | Blue Ice |  | 240 | 45W | 1 | 12.5.19 | 12 months | 12.5.20
307
308 | Broad Street Mess Room | Space Heater | ARGOS | DL10A | 230V | 2kW | 2 | 21.7.19 | 12 months | 21.7.20
309
310 | Broad Street Mess Room | Events Water Boiler (Stainless) | BURCO |  |  |  | 1 | 12.5.19 | 12 months | 12.5.20
311
312 | Broad Street Mess Room | Microwave Oven | Hitachi |  |  |  | 1 | 21.7.19 | 12 months | 21.7.20
313 | Broad Street Mess Room | Radio (Mess Room) | Technika |  |  |  | 2 | 12.5.19 | 12 months | 12.5.20
314 | Broad Street Mess Room | Coffee Maker | Russell Hobbs |  |  |  | 1 | Dispose? | As required | Expired |  | Not routinely tested
315
316
317 | Broad Street Cleaners Store | Vacuum Cleaner | Numatic | Henry | 230 | 1100W | 2 | 21.7.19 | 12 Months | 21.7.20
318 | Broad Street Cleaners Store | Vacuum Cleaner | VAX | 121 | 240 | 1kW | 1 | 21.7.19 | 12 months | 21.7.20
319
320 | Broad Street Cleaners Store | Vacuum Cleaner | TESCO |  | 240 |  | 2 | 21.7.19 | 12 months | 21.7.20
321 | Broad Street Museum | Vacuum Cleaner (Rechargeable) | BUSH | D35B1200200 |  | 6W | 2 | 21.7.19 | 12 months | 21.7.20
322 | Broad Street Media Store | Events Water Boiler (Galvanised) | BURCO |  |  |  | 1 | 2019-05-01 | As required | 2020-05-01
323
324 | Broad Street Mess Room | Fan Heater | Lervia | H3136 | 220-240V | 2kW | 2 | 21.7.19 | 12 months | 21.7.20 |  | First test 17.1.18
351
352 | Docks Mess Room | Toaster | TESCO |  | 240V | 1kW | 1 | 20.9.19 | 12 Months | 20.9.20
353
354
355 | Docks Mess Room | Portable radio | AIWA |  | 240V | 30W | 2 | 20.9.19 | 12 Months | 20.9.20
356 | Broad Street Mess Room | Fridge/Freezer | Hotpoint |  | 240V |  | 1 | 12.5.19 | 12 Months | 12.5.20 |  | Moved May 2018
357 | Docks Mess Room | Microwave Oven | TESCO |  | 240V |  | 1 | 20.9.19 | 12 Months | 20.9.20
358 | Docks Toilet | Vacuum Cleaner 1 | EARLEX | Martyn Evans | 240V |  | 2 | 20.9.19 | 12 Months | 20.9.20
359
360 | Docks Toilet | Vacuum Cleaner 3 | Rowenta |  | 240V |  | 2 | 20.9.19 | 12 Months | 20.9.20
361 | Docks Mess Room | Fan Heater | Phillips |  | 240V | 2kW | 2 | 20.9.19 | 12 Months | 20.9.20
362 | Docks Mess Room | Fridge/Freezer | Hotpoint |  | 240V |  | 1 | 20.9.19 | 12 Months | 20.9.20
363
364 | Docks Toilet | Vacuum Cleaner | Cyclonic |  | 240V | 1600W | 2 | 20.9.19 | 12 months | 20.9.20
365 | Docks Mess Room | Kettle | Bifinett |  | 240V |  | 2 | 20.9.19 | 12 months | 20.9.20
366 | Docks Mess Room | Ext Lead short 4 gang | LGA |  | 240V |  | 2 | 20.9.19 | 12 months | 20.9.20
367 | Docks Mess Room | Wall mounted heater | Dimplex |  | 240V |  | 1 | 20.9.19 | 12 months | 20.9.20
368 | Docks Mess Room | Hot water heater | Ariston |  | 240V | 5KW | 1 | 20.9.19 | 12 months | 20.9.20

## PAT Fault Log
Fail Log
Status | Ref No | Last Known Location | Description | Manufacturer | Model/Type | Volts | Watts/Amps | Class | FAIL DATE | Reason for Failure | Repairable? Y/N | Action | Notes
Current | 9 | Broad Street | Portable Power Drill | Black & Decker | H26 15 | 240V | 1.6A/370W | 2 | 12.4.17 | Cable Damaged | Y | Cable replaced
Current | 9 | Broad Street | Portable Power Drill | Black & Decker | H26 15 | 240V | 1.6A/370W | 2 | 16.1.18 | Frayed cable at entry point | Y | Shortened cable by 6"
Current | 10 | Broad Street | Portable Power Drill | Black & Decker | D520 | 200-250V | 1.3A/270W | 1 | 12.4.17 | Plug Damaged | Y | Plug replaced
Current | 13 | Broad Street | Portable Power Drill | Atlas Copco | 500R | 240V | 550W |  | 12.4.17 | Cable Damaged | Y | Cable replaced
Current | 31 | Broad Street | Inspection Light (Clamp) | Unknown | Tungsten | 230V |  | 1 | 10.8.17 | 6 months | FAIL | Earth Impedance 3 Ohm
Current | 42 | Broad Street | Extension Cable | PIFCO | 4m | 230V | 13A |  | 8.8.17 | Live wire off in socket | Y | Socket re-wired
Current | 43 | Broad Street | Extension Cable | Unmarked | 30m | 230V | 13A |  | 8.8.17 | Plug Damaged | Y | Plug replaced
Current | 49 | Broad Street | Portable Belt Sander | BLACKSPUR |  | 230V |  | 2 | 7.8.17 | Cable Damaged | Y | Cable replaced
Current | 77 | Broad Street | ARC Welder | Clarke | 190 | 240V |  | 1 | 10.8.17 | 12 months | Y | Plug Reterminated
Current | 203 | Broad Street | Bench grinder 1 | CLARKE | CBG8RWC | 230V | 375W | 1 | 10.8.18 | 12 months | Y | Plug Reterminated
Scrapped | 10 | Broad Street | Portable Power Drill | Black & Decker | D520 | 200-250V | 1.3A/270W | 1 | 7.8.17 | 6 months | 7.2.18 | 115 MOhm Leakage | Failed- Open Cct Field Coils 17.9.17
Scrapped | 39 | Broad Street | Extension Cable | RED | 50m | 230V | 13A |  | 8.8.17 | Previous damage- Improper repair. | N | Scrapped
Scrapped | 40 | Broad Street | Extension Cable | MASTER PLUG | 30m | 230V | 13A |  | 8.8.17 | Previous damage- Improper repair. | N | Scrapped
Scrapped | 64 | Broad Street | Mains short extension & 4-way splitter | Unknown | 1m | 230V | 13A |  | 7.8.17 | Impact Damage | N | Scrapped
Scrapped | 112 | Docks | Extension Cable 3 | Unknown | 30m | 240V |  |  | 12.9.17 | Cable damage | FAIL | Scrapped
Scrapped | 307 | Broad Street Mess Room | Space Heater | Connect-IT | ES126 | 230V | 1050W | 1 | 17.1.18 | Case partially melted. | FAIL | Scrapped
Vanished | 317 | Broad Street Mess Room | DC adaptor for Portable TV | Maxim |  |  |  | 2 |  | 12 months | Disposed of? | Out of Use
Vanished | 309 | Broad Street Mess Room | Travel Iron | Morphy Richards | 41300 | [5 empty] | Disposed of?
Vanished | 305 | Broad Street Mess Room | VHS Recorder/Player | Panasonic |  |  |  | 1 |  | 12 months | Disposed of?
Vanished | 315 | Broad Street Mess Room | Coffee Maker | Prima |  |  |  | 1 | Dispose? | 12 months | Disposed of? | Out of Use
Scrapped | 311 | Broad Street Mess Room | Fridge | Zanussi |  |  |  | 1 | 11.4.18 | 12 months | 11.4.19 | Failed May 2018- Scrapped
Scrapped | 63 | Broad Street | Mains short extension & 4-way splitter | Unknown |  | 230V | 13A |  | 8.8.18 | Earth Leakage | 75Mohm | Monitoring | Units Incorporates Suppression Filter
Scrapped | 38 | Broad Street | Extension Cable | RED | 50m | 230V | 13A | 1 | 8.8.18 | 12 months | Disposed | Cable damage & bent reel | Earth Impedance 0.4 Ohm
Scrapped | 29 | Broad Street | Work Light (with Floor stand) | Screwfix | Tungsten | 230V | 2x 500W | 1 | 10.8.18 | 12 months | Disposed
Scrapped | 30 | Broad Street | Work Light (with Floor stand) | Unknown | Tungsten | 230V | 500W | 1 | 10.8.18 | 12 months | Disposed
Scrapped | 31 | Broad Street | Inspection Light (Clamp) | Unknown | Tungsten | 230V |  | 1 | 10.8.18 | 6 months | Disposed
Scrap | 316 | Broad Street Mess Room | Slow Cooker | Breville | Unknown | 230 |  | 1 | 30.4.17 | Earth Leakage | 87Mohm | Monitoring | Scrap
Scrapped | 206 | Broad Street | Bench Pillar Drill | WOLF | NWC3E | 220-250V | 750W | 1 | 8.8.18 | 12 months | 8.8.19 | Plug removed failed test
Scrapped | 6 | Broad Street | Portable Radio/CD Player | ALBA | CX440/A | 230/240V |  | 2 | 8.8.18 | 12 months |  |  | Scrapped
Scrapped | 45 | Broad Street | Portable Sander | JCB |  | 230V |  | 2 | 7.8.18 | 12 months | Scrapped |  | Not found since Summer 2018
Scrapped | 46 | Broad Street | Portable Sander | JCB |  | 230V |  | 2 | 7.8.18 | 12 months | Scrapped |  | Not found since Summer 2018
Scrapped | 47 | Broad Street | Portable Sander | JCB |  | 230V |  | 2 | 7.8.18 | 12 months | Scrapped |  | Not found since Summer 2018
Scrapped | 48 | Broad Street | Portable Sander | SANDCRITTER | CLM105 | 230V | 105W | 2 |  | 12 months | Scrapped
Scrapped | 71 | Broad Street | Handheld Circular Saw | Black & Decker | DNJ70N | 240V | 370W | 2 |  | 12 months | Scrapped
Scrapped | 319 | Broad Street Cleaners Store | Vacuum Cleaner | DYSON | 802A | 240 |  | 2 | 21.7.19 | 12 months | 21.7.20 | Scrapped
Scrapped | 206 | Broad Street | Bench Pillar Drill | WOLF | NWC3E | 220-250V | 750W | 1 | 6.9.19 | 12 months | Fail | Plug removed failed test
Removed | 109 | Docks | Battery Charger/Starter 2 | SIP 25082 | 500/50 | 230V | 3kW? | 1 | 6.8.18 | 12 months | 6.8.19 | Into Stock 7/18 | Removed from site
Scrapped | 103 | Docks | Pressure Washer | Brook Crompton |  | 240V |  |  | 12.9.17 | 12 months | 12.9.18 |  | Scrapped
Scrapped | 105 | Docks | Steam Cleaner | Burton | 300HM | 240V | 2.2Kw | 1 |  |  |  | Into Stock 7/18 | Scrapped
Scrapped | 107 | Docks | Pressure Washer (Max 80C) | Karcher | HDS 601C | 240V | 3.2kW | 1 | Fail |  |  | Into Stock 7/18 | Scrapped
Scrapped | 74 | Broad Street | MIG Welder | MIGMATE |  | 240V |  | 1 | 10.8.17 | 12 months | 10.8.18 |  | scrap
Scrapped | 351 | Docks Mess Room | Kettle | TESCO | JK07 | 240V | 2kW | 1 | 12.9.17 | 12 Months | 12.9.18 |  | scrap
Scrapped | 353 | Docks Mess Room | Heater | Dunelm |  | 240V | 2kW | 1 | 15.9.18 | 12 Months | 15.9.19 | Leakage 50M Ohm | scrap
Scrapped | 354 | Docks Mess Room | Radio- Mess room | Sharp |  | 240V | 30W | 2 | 15.9.18 | 12 Months | 15.9.19 | Scr
Scrapped | 359 | Docks Toilet | Vacuum Cleaner 2 | Panasonic |  | 240V |  | 2 | 12.9.17 | 12 Months | 12.9.18 | Scr
Missing | 363 | Docks Mess Room | 13A 3 way Splitter | Volex |  | 240V | n/a | n/a | 12.9.17 | 12 Months | 12.9.18 | Missing
Missing | 7 | Broad Street | Portable Jigsaw | Black & Decker | KS500 | 230V | 400W | 2 | 7.8.17 | 6 months | 7.2.18 |  | Missing
Scrapped | 51 | Broad Street | Trolley Compressor | Clarke |  | 240V |  | 1 | 7.8.18 | 12 months | 8.8.19 |  | Scr
Scrapped | 59 | Broad Street | Tyre Cutter | Unknown |  | 230V |  | 1 | 7.8.17 | 12 months | 7.8.18 |  | Scr
Scrapped | 66 | Broad Street | Detail Sander | Rally |  | 230V | 180W | 2 | 7.8.18 | 12 months | 8.8.19 |  | Scr
Scrapped | 106 | Docks | Angle Grinder 1 | Parkside | PWS125 | 240V |  |  | Due |  |  |  | Scr
Scrapped | 110 | Docks | Extension Cable 1 | MASTERPLUG WORKPOWER | 45m | 240V |  |  | 20.9.19 | 12 months | 20.9.20 |  | Scrapped due to damage
Scrapped | 111 | Docks | Extension Cable 2 | MASTERPLUG WORKPOWER | 45m | 240V |  |  | 12.9.17 | 12 months | 12.9.18 |  | Awaiting repair off site 9/19
Notable Results Log
[11 empty] | Measured Value | Action | Notes
Status | Ref No | Last Known Location | Description | Manufacturer | Model/Type | Volts | Watts/Amps | Class | Test Date | Marginal Parameter | 160Mohm | Monitoring
Current | 9 | Broad Street | Portable Power Drill | Black & Decker | H26 15 | 240V | 1.6A/370W | 2 | 10.2.18 | Earth Leakage | 115Mohm | Monitoring
Current | 10 | Broad Street | Portable Power Drill | Sealey |  | 200-250V |  | 2 | 10.2.18 | Earth Leakage | 130 Mohm Leakage | Monitoring
Current | 25 | Broad Street | Soldering Iron | ???LOGIC |  | 240V | 30W | 1 | 10.8.17 | Earth Leakage | 61 Mohm | Monitoring
Current | 207 | Broad Street | Parts Degreaser |  |  | 240V |  | 1 | 7.8.17 | Earth Leakage
[11 empty] | 50Mohm | Monitoring
Current | 353 | Docks | Heater | Dunelm |  | 240V | 2kW | 1 | 12.9.17 | Earth Leakage | 80Mohm | Monitoring
Current | 363 | Docks | 13A 3 way Splitter | Volex |  | 240V | n/a | n/a | 12.9.17 | Earth Leakage

## FLT
FLT
Ref | Location | Type and description | Fuel | SWL | Inspection Date
FLT01 | Broad Street | Mitsibishi | LPG | 3T | 2020-03-09
FLT02 | Windward | Coventry Climax | LPG | 3T | 2020-04-01

## Ladders
LADDERS
Ref | Location | Type and description | Inspection Date
L1 | Broad St | 0.5m step ladder - Aluminium | 2020-03-09
L2 | Broad St | 3.4m extendable ladder - Aluminium | 2020-03-09
L3 | Broad St | 2m step ladder - Aluminium | 2020-03-09
L4 | Broad St | 1.5m step ladder - Steel | 2020-03-09
L5 | Windward | 0.5m step ladder - Steel | 2020-03-09
L6 | Windward | 1m step ladder - Aluminium | 2020-03-09
L7 | Windward | 2.5m step ladder - Aluminium | 2020-03-09
L8 | Windward | 3m extendable ladder - Aluminium | 2020-03-09
L9 | Windward | 3.1m extenable ladder - Aluminium | 2020-03-09
Walking steps & Platforms
Ref | Location | Type and description | Inspection Date
PL1 | Broad St | 2.7m UTS tower - Aluminium | 2020-03-09
PL2 | Broad St | 2.5m walking steps - Aluminium | 2020-03-09
PL3 | Broad St | 0.75m walking steps - Aluminium | 2020-03-09
PL4 | Broad St | 1.5m platform - Aluminium | 2020-03-09
PL5 | Broad St | 2.65m walking steps - Steel | 2020-03-09
PL6 | Broad St | 0.75m walking steps - Steel | 2020-03-09
PL7 | Broad St | 0.75m walking steps - Steel | 2020-03-09
PL8 | Broad St | 0.75m walking steps - Steel | 2020-03-09
PL9 | Windward | 2m walking steps - Steel | 2020-03-09

## Fire Extinguishers
BROAD STREET DEPOT
|  |  | Inspected | Fault
Area Description | Equipment | Ref.No | or Tested | Y/N | Checked | Remarks
Canteen | Fire Blanket |  | Inspected | N | 2020-03-09 | Purchased 2008
Museum wall | 6Kg Dry Powder | D1 | Inspected | N | 2020-03-09 | Purchased 2008
Door 5 | 9Kg Dry Powder | D2 | Inspected | N | 2020-03-09 | Purchased 2008
South Wall benches | 6Kg Dry Powder | D3 | Inspected | N | 2020-03-09 | Purchased 2015
Pit stairs | 6Kg Dry Powder | D4 | Inspected | N | 2020-03-09 | Purchased 2008
Pit fire exit | 6Kg Dry Powder | D5 | Inspected | N | 2020-03-09 | Purchased 2008
WINDWARD DEPOT
|  |  | Inspected | Fault
Area Description | Equipment | Ref.No | or Tested | Y/N | Cleared | Remarks
Toilet Wall | 6Kg Dry Powder | AT1 | Inspected | N | 2020-03-09 | Purchased 2015
Pit area | 6Kg Dry Powder | AT2 | Inspected | N | 2020-03-09 | Purchased 2015
Mid Depot | 6Kg Dry Powder | AT3 | Inspected | N | 2020-03-09 | Purchased 2015
Back room | 6Kg Dry Powder | AT4 | Inspected | N | 2020-03-09 | Purchased 2015

## First Aid
First Aid Box
Ref | Location | Inspection Date | Replacement date
FA1 | Broad St Canteen | 2020-05-02 | 2022-12-01
FA2 | Windward canteen | 2020-05-02 | 2022-12-01
FA3 | Broad Street | 2020-05-09 | 2021-05-01
FA4 | Broad Street | 2020-05-09 | 2022-09-01
FA5 | Windward pits | 2020-05-09 | 2021-05-01
FA6 | Windward front door | 2020-05-09 | 2021-05-01